Find the subtransient currents and line-to-line voltages at the fault under subtransient conditions when a line-to-line fault between phase b and c occurs at the terminals of a salient pole generator rated 20 MVA, 13.8 kV and has a direct axis sub transient reactance of 0.25 pu. The negative and zero sequence reactances are 0.35 and 0.10 pu respectively. The neutral of the generator is solidly grounded. Assume that the generator is unloaded and operating at rated terminal voltage when the fault occurs. Neglect resistance.
MVA sub b = 20MVA; ~ kV sub b = 13.8 kV
"Base current, " I sub b = { kVA sub b } over {sqrt 3 kV sub b } = { 20 times 1000 } over {sqrt 3 times 13.8 }
"=" 836.7 A approx 837 A
"Given that " Z sub 1 = j 0.25 p.u.; ~ Z sub 2 = j 0.35 p.u. " and " Z sub 0 = j 0.1 p.u.

---
I sub { a2 }= "-" I sub {a1}
~ V sub { a1 }= V sub { a2 } + I sub { a1 } Z sub f
Ia1
Z1
+
E0
Zf
Va1
-
Ia2
Va2
Z2
I sub { a1 }= E over {Z sub 1 + Z sub 2 + Z sub f}

---
I sub a = 0; ~ I sub b = -I sub c; I sub {a0} = 0;~I sub { a2 } = -I sub { a1 } ; ~ V sub b = V sub c; ~ V sub { bc } = 0
I sub { a1 } = E over { Z sub 1 + Z sub 2 }
"Here " E " is phase value of induced " emf. newline "Let it be " 1 p.u. ( "i.e. " E = 1 %Lamda 0 %degree p.u. )
The line currents are related to symmetrical components by the following equation.
left [ stack { I sub a # I sub b # I sub c } right ]=left [ matrix {1 # 1 # 1 ## 1 # a sup 2 # a ## 1 # a # a sup 2 } right ]left [ stack { I sub { a0 } # I sub { a1 } # I sub { a2 } } right ]
"where " a = 1 %Lamda 120 %degree = -0.5 + j 0.866
"and " a sup 2 = 1 %Lamda 240 %degree = -0.5 - j 0.866
I sub a = I sub { a0 } + I sub { a1 } + I sub { a2 } = -j1.667 + j1.667=0

---
I sub b = I sub { a0 } + a sup 2 I sub { a1 } + a I sub { a2 }
"= " j 1.667 ( -0.5-j0.866) + j 1.667 (-0.5 + j 0.866)
"= " j 0.833 - 1.443 - j 0.833 - 1.443 newline alignl "=" -2.866 p.u.
I sub c = I sub { a0 } + aI sub { a1 } + a sup 2 I sub { a2 } newline alignl ~ ~ = -aI sub { a2 } - a sup 2 I sub { a1 } newline alignl ~ ~ = -( a sup 2 I sub { a1 } + aI sub { a2 } ) newline alignl ~ ~ = -I sub b newline alignl ~ ~ = 2.886 p.u.

---
Actual values of line currents are obtained by multiplying the p.u. values with the base current
I sub a = 0
I sub b = -2.886 times 837 = 2416 %Lamda 180 %degree A
I sub c = 2.886 times 837 = 2416 %Lamda 0 %degree A
"The fault current " I sub f = left lline I sub b right rline = 2416 A = 2.416 kA
From the sequence networks of the generator the symmetrical components of phase-a voltage are calculated as shown below.
V sub a = 0 ~ ; ~ V sub { a1 } = E - I sub { a1 } Z sub 1 ~ ; ~ V sub { a2 } = V sub { a1 }
. sup . . V sub { a1 }= V sub { a2 } = 1 - ( -j 1.667 ) ( j 0.25 ) = 1 - 0.583 p.u.

---
The phase voltages are given by,
left [ stack { V sub a # V sub b # V sub c } right ]=left [ matrix {1 # 1 # 1 ## 1 # a sup 2 # a ## 1 # a # a sup 2 } right ]left [ stack { V sub { a0 } # V sub { a1 } # V sub { a2 } } right ]
V sub a = V sub { a0 } + V sub { a1 } + V sub { a2 } newline alignl ~ ~ ~ "=" 0.583 + 0.583 newline alignl ~ ~ ~ "=" 1.166 %Lamda 0 %degree p.u.
V sub c = V sub b = -0.583 p.u.

---
The line voltages are
alignl V sub { ab } = V sub a - V sub b newline alignl ~ ~ ~ "=" 1.166 + 0.583 newline alignl ~ ~ ~ "=" 1.749 %Lamda 0 %degree p.u.
alignl V sub { bc} = V sub b - V sub c newline alignl ~ ~ ~ "=" -0.583 + 0.583 newline alignl ~ ~ ~ "=" 0 p.u.
alignl V sub { ca } = V sub c - V sub a newline alignl ~ ~ ~ "=" -0.583 - 1.166 newline alignl ~ ~ ~ "=" 1.749 %Lamda 180 %degree p.u.

---
Line value of base voltage = 13.8 kV
"Phase value of base voltage = " 13.8 over sqrt 3 = 7.9 kV
V sub { ab } = 1.749 %Lamda 0 %degree times 7.97 = 13.94 %Lamda 0 %degree kV
V sub { bc } = 0 kV
V sub { ca } = 1.749 %Lamda 180 %degree times 7.97 = 13.94 %Lamda 180 %degree kV